**Effective July 10, 2021 the State of Washington has adopted the following additional rules**

**[this informational page may be removed by jurisdictions utilizing the standard conditions]:**

5707.1.2 Coordination of permits. Permits across multiple authorities having jurisdiction shall be coordinated in accordance with Sections 5707.1.2.1 through 5707.1.2.4.

5707.1.2.1 Acceptance of permits issued by other authorities having jurisdiction. Local authorities having jurisdiction that allow mobile on demand fueling trucks may accept conforming permits issued and/or inspections performed by any other local authorities having jurisdiction in Washington state. Local authorities having jurisdiction that choose to accept conforming permits issued by other local authorities having jurisdiction in Washington state retain the right to enforce the provisions of this section.

5707.1.2.2 Local authorities having jurisdiction not offering operator or truck certification. A conforming operator or vehicle permit issued by one local authority having jurisdiction shall be recognized and accepted by all local authorities having jurisdiction in Washington state, if those local authority having jurisdictions allow mobile on demand fueling and do not offer such operator or truck certification. Under no circumstances will an issuing local authority having jurisdiction be expected to perform permissive inspections beyond their jurisdiction.

5707.1.2.3 Commencing permit issuance. When a local authority having jurisdiction that has previously authorized mobile fueling operations but not issued their own permits commences permit issuance for mobile fueling operations or vehicles, that local authority having jurisdiction shall continue to accept permits previously issued by another local authority having jurisdiction in Washington state for three months or until their expiration date, whichever is sooner.

5707.1.2.4 Permit record maintenance. Issuing local authorities having jurisdiction shall maintain a publicly available list of current permits or other information source to enable all parties to have information about whether permits are in good standing.

**2018 WA State Fire Code Conditions**

**This permit shall be kept on the premises designated herein at all times and shall be readily available for inspection by the fire code official.** [WA State Fire Code Section 105.3.5]

1. On-Demand Mobile Fueling shall only be from fueling vehicles approved by the Fire Code Official. Each fueling vehicle shall have a separate permit. [WA State Fire Code Section 105.6.16 #6 and 105.7.9]
2. On-Demand Mobile Fueling shall only be conducted at sites that have an operational permit issued by the Fire Code Official. [WA State Fire Code Section 105.6.16 #11]
3. On-Demand Mobile Fueling shall not occur on public streets, public ways, inside of buildings or on the roof or inside of any parking structure. [WA State Fire Code Section 5707.4]
4. Mobile fueling operators shall have an *approved* written safety and emergency response plan that establishes policies and procedures for fire safety, spill prevention and control, personnel training and compliance with other applicable requirements of this code. [WA State Fire Code Section 5707.3.1]
5. Mobile fueling vehicles shall be operated only by designated personnel who are trained on proper fueling procedures and the safety and emergency response plan. Training records of operators shall be maintained. [WA State Fire Code Section 5707.3.2]
6. Mobile fueling vehicles shall be constantly attended during fueling operations with brakes set and warning lights in operation. Mobile fueling vehicles shall not obstruct emergency vehicle access roads. [WA State Fire Code Section 5707.6]
7. Mobile fueling vehicles shall be positioned in a manner to preclude traffic from driving over the dispensing hose. The dispensing hose shall be properly placed on an approved reel or in an approved compartment prior to moving the mobile fueling vehicle. [WA State Fire Code Section 5707.6.1]
8. Operators shall place a drip pan or an absorbent pillow under the nozzle and each fuel fill opening prior to and during dispensing operations to catch drips. [WA State Fire Code Section 5707.6.2]
9. Safety cones or other visual barriers shall be employed as warning devices to highlight the vehicle fueling area. Signs prohibiting smoking or open flames within 25 feet shall be prominently posted in the vehicle fueling area. [WA State Fire Code Section 5707.6.3]
10. The mobile fueling vehicle flasher lights shall be in operation while dispensing operations are in progress. [WA State Fire Code Section 5707.6.4]
11. The mobile fueling vehicle and its equipment shall be maintained in good repair. [WA State Fire Code Section 5707.2.2(2)]
12. Safety cans and approved metal containers shall be secured to the mobile fueling vehicle except when in use. [WA State Fire Code Section 5707.2.2(3)]
13. Fueling a motor vehicle from tanks or containers mounted in a trailer connected to a mobile fueling vehicle is prohibited. [WA State Fire Code Section 5707.2.2 (4)]
14. Nighttime deliveries shall only be made in areas adequately lighted per WAC 296-800-21005. [WA State Fire Code Section 5707.6.5]