**Effective July 10, 2021 the State of Washington has adopted the following additional rules**

**[this informational page may be removed by jurisdictions utilizing the standard conditions]:**

5707.1.2 Coordination of permits. Permits across multiple authorities having jurisdiction shall be coordinated in accordance with Sections 5707.1.2.1 through 5707.1.2.4.

5707.1.2.1 Acceptance of permits issued by other authorities having jurisdiction. Local authorities having jurisdiction that allow mobile on demand fueling trucks may accept conforming permits issued and/or inspections performed by any other local authorities having jurisdiction in Washington state. Local authorities having jurisdiction that choose to accept conforming permits issued by other local authorities having jurisdiction in Washington state retain the right to enforce the provisions of this section.

5707.1.2.2 Local authorities having jurisdiction not offering operator or truck certification. A conforming operator or vehicle permit issued by one local authority having jurisdiction shall be recognized and accepted by all local authorities having jurisdiction in Washington state, if those local authority having jurisdictions allow mobile ondemand fueling and do not offer such operator or truck certification. Under no circumstances will an issuing local authority having jurisdiction be expected to perform permissive inspections beyond their jurisdiction.

5707.1.2.3 Commencing permit issuance. When a local authority having jurisdiction that has previously authorized mobile fueling operations but not issued their own permits commences permit issuance for mobile fueling operations or vehicles, that local authority having jurisdiction shall continue to accept permits previously issued by another local authority having jurisdiction in Washington state for three months or until their expiration date, whichever is sooner.

5707.1.2.4 Permit record maintenance. Issuing local authorities having jurisdiction shall maintain a publicly available list of current permits or other information source to enable all parties to have information about whether permits are in good standing.

**2018 WA State Fire Code Conditions**

**This permit shall be kept on the premises designated herein at all times and shall be readily available for inspection by the fire code official.** [WA State Fire Code Section 105.3.5]

1. An operational permit is required to utilize a site for On-Demand Mobile Fueling operations. [WA State Fire Code Section 105.6.16 #11]
2. The approval of the owner of the site shall be obtained to conduct On-Demand Mobile Fueling and documentation shall be provided to the fire code official. [WA State Fire Code Section 105.1.1]
3. Where required by the fire code official, a site plan shall be developed for each location at which mobile fueling occurs. The site plan shall be in sufficient detail to indicate: all buildings, structures, lot lines, property lines, electric car chargers, solar photovoltaic parking lot canopies, and appurtenances on site and their use or function; all uses adjacent to the lot lines of the site; fueling locations, the locations of all storm drain openings and adjacent waterways or wetlands; information regarding slope, natural drainage, curbing, impounding and how a spill will be kept on the site property; and the scale of the site plan. [WA State Fire Code Section 5707.3.3]
4. Where a site permitting process is required by the fire code official, a site shall be designated by the fire code official to be a Tier 1 or Tier 2 site. A Tier 1 site does not present atypical geographic, safety or environmental concern and shall be provided with expedited permitting review and shall allow permit issuance prior to site inspection. The fire code official may impose additional conditions and may perform a site inspection during the period of permit validity of a Tier 1 site. A Tier 2 site does require an inspection by the fire code official and shall be approved prior to permit issuance. [WA State Fire Code Section 5707.3.4 through 5707.3.4.2]
5. Engaging in the dispensing of fuel into vehicles at this location shall only be conducted by an On-Demand mobile fueling company who has a valid On-Demand mobile fueling operational permit issued by the fire code official. [WA State Fire Code Section 105.6.16 #10]
6. Mobile Fueling on an approved site shall only be from fueling vehicles approved by the fire code official. Each fueling vehicle shall have a separate permit. [WA State Fire Code Section 105.6.16 #6 and 105.7.9]
7. The mobile fueling operation and the point of connection of the vehicle being fueled shall not occur on public streets, publicways or inside buildings. Mobile Fueling on the roof level of parking structures or other buildings is prohibited. [WA State Fire Code Section 5707.4]
8. Mobile fueling shall not take place within 25 feet (7620 mm) of buildings, lot lines, property lines or combustible storage.

**Exception:**

The fire code official shall be authorized to decrease the separation distance for dispensing from metal safety cans or other approved metal containers.

[WA State Fire Code Section 5707.4.1]

1. Smoking, open flames and other sources of ignition shall be prohibited within 25 feet (7620 mm) of fuel dispensing activities. Signs prohibiting smoking or open flames within 25 feet (7620 mm) of the vehicle or the point of fueling shall be prominently posted on the mobile fueling vehicle. The engines of vehicles being fueled shall be shut off during fueling. [WA State Fire Code Section 5707.4.2]
2. Mobile fueling shall not occur within 20 feet of electrical equipment located within 18 inches of the ground unless such electrical equipment is rated for Class 1, Division 2 hazardous locations in accordance with NFPA 70. [WA State Fire Code Section 5707.4.2]